## Slide 1
COMPUTE ATLAS · DECK 1 OF 2 · PROBLEM, INSPIRATION, FACTS
Before you build an AI factory,
prove the site can support it.
Why siting AI data centres in India is an evidence problem, not a map problem — and why the answer has to say what it does not know.
Prepared for the Bhopal Claude Code Build Day · 20 September 2026 · Every external figure carries its source; forecasts are labelled as forecasts.
1 / 19

## Slide 2
THE HOOK
Source: Anthropic API rate-limit documentation
2 / 19
Ever hit a rate limit while building?
Capacity is part of the story. So are usage tiers, spend controls and abuse prevention — Anthropic's own documentation lists all of them.
Whatever the policy, every AI response still has a physical address. Somewhere, chips need electricity, cooling and a network.
So: where should the next facility go — and how would you know the site can carry it?
Notes: Start with a familiar developer experience. Rate limits have several causes; do not equate every limit with a GPU shortage. Then pivot: whatever the product policy, serving AI needs physical infrastructure. Source: https://platform.claude.com/docs/en/api/rate-limits

## Slide 3
WHAT COMPUTE ACTUALLY IS
Compute Atlas · Bhopal Claude Code Build Day · 20 September 2026
3 / 19
A GPU order does not create usable compute.
Delivering compute at scale is a chain of physical dependencies. Every link has to hold at a specific place.
CHIPS & NETWORKING
the part everyone talks about
DEPENDABLE ELECTRICITY
at full load, on a date, under contract
HEAT REMOVAL
cooling design, water or dry systems
LAND & PERMISSION
net buildable area, zoning, rights
CONNECTIVITY
fibre routes, diversity, latency
OPERATIONS & CAPITAL
people, uptime, financing
Notes: Compute is processing infrastructure for training and inference. A GPU order does not by itself create usable capacity.

## Slide 4
WHY NOW · FORECAST, NOT A MEASUREMENT
Source: IEA, Energy and AI updated outlook (2026)
4 / 19
Data-centre electricity demand is projected to nearly double.
485 TWh → 950 TWh
2025
2030 · about 3% of global electricity demand
READ IT CAREFULLY
This is a projection of consumption, not metered demand. The same outlook flags supply-chain bottlenecks and uncertain investment returns. Growth in demand is exactly why the siting question gets harder, not easier.
Notes: IEA updated projection for global data-centre electricity consumption; roughly 3% of global demand by 2030. All data centres, not only AI. Use this consumption series consistently; do not mix with the older report's generation figures. Source: https://www.iea.org/reports/key-questions-on-energy-and-ai/executive-summary

## Slide 5
SOFTWARE BECAME HEAVY INDUSTRY · THIRD-PARTY FIGURES
Source: "AI Token Factory" video presentation (YouTube) · figures as stated in the video, not independently verified by us
5 / 19
Software used to have zero marginal cost. Now it is measured in megawatts.
2026 AI INFRASTRUCTURE SPEND · FOUR HYPERSCALERS
$725B
About 1.2× the inflation-adjusted cost of the entire US Interstate Highway System, in one year.
PROJECTED BUILD-OUT 2026–2031
$7.6T
Goldman Sachs projection as cited in the video. A projection, not a commitment.
COST PER QUERY · GENERATION VS SEARCH
10–100×
Search retrieves from an index. A model computes every word from scratch.
Google is a librarian. It finds a page that already exists, in milliseconds, for a fraction of a cent. A model is a writer. It runs hundreds of billions of arithmetic operations to produce each token, then does it again for the next one. That labour is electricity, and electricity has an address.
Notes: Figures as stated in the 'AI Token Factory' presentation: the four largest US tech companies projected to spend about $725 billion on AI infrastructure in 2026, described as 1.2x the inflation-adjusted cost of the US Interstate Highway System; Goldman Sachs projection of $7.6 trillion of build-out 2026-2031. We have not verified these against primary sources; say 'as reported in the video'. The librarian/writer framing: search retrieves from an index for fractions of a cent; generation computes every word, 10x to 100x the cost per query. Source: https://www.youtube.com/

## Slide 6
THE TRIP · WHAT HAPPENS TO ONE QUESTION
Source: "AI Token Factory" video presentation (YouTube) · figures as stated in the video, not independently verified by us
6 / 19
Every prompt takes a physical trip. Four of its six steps happen inside one building.
INSIDE THE DATA CENTRE · THE BUILDING WE ARE SITING
1 · The trip out
Radio to a tower, then light through fibre at about ⅔ the speed of light.
2 · The front door
An API gateway checks identity, limits and loads the conversation context.
3 · Tokenisation
Text is chopped into numeric pieces, about ¾ of a word each.
4 · Prefill
The model reads the whole prompt at once and builds its working memory, the KV cache.
5 · Decode
One token at a time. The entire network runs for every single word.
6 · The trip home
Tokens stream back to the device the same way they came.
The network is fast and the device is cheap. The expensive, slow, physical part of the trip is the building in the middle: its power feed, its cooling, its fibre and the years it takes to get all three.
Notes: Six-step journey of a query as described in the video. Steps 2 to 5 all happen inside a data centre: the API gateway, tokenisation, prefill (building the KV cache, the model's working memory) and decode (one token at a time, the whole network run for every word). Point at the middle four boxes: that is the building we are siting. Fibre carries light at roughly two thirds of the speed of light in vacuum. Source: https://www.youtube.com/

## Slide 7
WHERE THE BOTTLENECK IS NOW · THIRD-PARTY FIGURES
Source: "AI Token Factory" video presentation (YouTube) · figures as stated in the video, not independently verified by us
7 / 19
Chips ship eventually. The next bottleneck is the building.
POWER PER RACK
10 → 120 kW
A traditional rack draws 5–10 kW; an Nvidia GB200 rack about 120 kW. Next generation projected near 600 kW.
GRID INTERCONNECTION WAIT
4–5 years
US queue times as stated. The grid was built for 1–2% annual growth.
TRANSFORMER LEAD TIME
1 → ~4 years
High-voltage transformers, from about a year to nearly four.
AIR COOLING GIVES OUT AT
30–50 kW
Per rack. Beyond that, liquid cooling is mandatory, and liquid means water design.
Layer by layer, the constraint has moved down the stack. Chips, high-bandwidth memory and networking are supply-chain problems: scarce, expensive, but they ship. The grid connection, the substation, the transformer and the heat rejection do not ship. They are built, permitted and energised at one specific place over years. That is a siting problem. India's grid, approvals and water differ from the US, so these numbers are the shape of the problem, not local values. The local values are exactly what nobody has in one place.
Notes: As stated in the video, for the US market: a traditional rack draws 5-10 kW; an Nvidia GB200 rack about 120 kW; next-generation Vera Rubin projected around 600 kW. Air cooling is effective to roughly 30-50 kW per rack, so flagship racks require liquid cooling. Grid interconnection queues of 4-5 years; high-voltage transformer lead times from about 1 year to nearly 4. PUE around 1.1 for modern liquid-cooled facilities versus near 2.0 for older ones. Chips, memory and networking are supply-chain problems that ship eventually; the building, its grid connection and its heat rejection are the gating item, and that is a siting problem. India's grid and approvals differ, so treat the numbers as the shape of the problem, not local values. Source: https://www.youtube.com/

## Slide 8
WHY INDIA · DATED GOVERNMENT STATEMENT
Source: PIB, IndiaAI compute empanelment (March 2026)
8 / 19
India is expanding compute access — and will need places to put it.
GPUS EMPANELED · MARCH 2026
38,000+ through 14 providers
Another 20,000 were being added under a process then underway.
WHAT THAT DOES NOT MEAN
Empaneled is not continuously available. The hardware is heterogeneous. It is a dated statement about a procurement pool, not a live capacity meter.
The opportunity is access plus execution: helping capable teams turn ambitions into sites whose dependencies are understood. Local-language applications, research and industry can benefit from domestic access. Construction alone guarantees none of it.
Notes: IndiaAI reported more than 38,000 GPUs empaneled through 14 providers in March 2026, with another 20,000 being added under a process then underway. Empaneled capacity is not continuously available capacity and not a homogeneous benchmark. Source: https://www.pib.gov.in/PressReleasePage.aspx?PRID=2239614&lang=2&reg=3

## Slide 9
A DEFENSIBLE ECONOMIC STORY
Compute Atlas · Bhopal Claude Code Build Day · 20 September 2026
9 / 19
Compute is an enabling input, not a scoreboard.
Accessible compute
›
Experimentation & locally relevant services
›
Industrial adoption
›
Value — only with demand, skills, software and viable economics
We do not claim: "countries with the most compute are the most profitable." No league table exists that normalises accelerator capability, utilisation, cloud imports and exports, cost and adoption.
We do claim: hosting capacity, owning chips, operating a cloud profitably and capturing national value are four different things. Our product touches the first one: can this site host it at all?
Notes: Do not claim that countries with the most compute are the most profitable. Countries have no company-style profit measure and correlation would not establish causation. Compute is one enabling input.

## Slide 10
INSPIRATION · CRUSOE
Source: Crusoe Series F announcement, 17 September 2026
10 / 19
Start with energy, then ask what compute it can carry.
Energy-first. Crusoe's early strategy brought computing to energy sources, including stranded gas, instead of assuming every workload starts at a conventional data-centre location.
Two facility sizes. Large campuses and Spark, a prefabricated modular AI data centre integrating power, cooling, racks, monitoring and fire suppression (introduced 26 June 2025).
Investor conviction. 17 September 2026: initial closing of an anticipated $3.9 billion Series F at a $30.9 billion post-money valuation.
“controlling the infrastructure from electrons to tokens”
Chase Lochmiller, Crusoe funding release, 17 Sep 2026
KEPT HONEST
Funding and valuation signal investor commitment, not audited profit. Spark's delivery speed is a vendor claim. We are a software screening product with no affiliation to Crusoe.
Notes: Founders Chase Lochmiller and Cully Cavness. Early strategy brought computing to energy sources including stranded gas. Spark introduced 26 June 2025 as a prefabricated modular AI data centre; 'as fast as three months' is a vendor claim. Series F: initial closing of an anticipated $3.9B round at $30.9B post-money, announced 17 September 2026. Funding is not profit. Compute Atlas has no affiliation with Crusoe. Spark is not a nuclear reactor. Source: https://www.crusoe.ai/resources/newsroom/crusoe-announces-series-f-funding

## Slide 11
WHAT WE BORROW INTELLECTUALLY
Compute Atlas · Bhopal Claude Code Build Day · 20 September 2026
11 / 19
Five ideas we took from the energy-first playbook.
01
Workload and energy together
Never evaluate the site without the load it must carry.
02
Campus versus modular
Compare centralised and distributed deployment where it makes sense.
03
Time to usable capacity
Energisation date matters as much as land price.
04
Potential ≠ deliverable power
Annual renewable potential is not hourly reliability.
05
Move compute toward energy
Only if latency, network and operations still hold.
Nuclear and flare-gas supply stay research scenarios. Proximity to a generator is never a supply contract. Flexible batch training and latency-sensitive inference do not share uptime requirements.
Notes: These principles shape the product; they are not endorsements of any energy scenario. Nuclear and flare-gas remain research scenarios needing specialist engineering and approvals.

## Slide 12
THE FACTS OF A SITE · ILLUSTRATIVE ARITHMETIC
Compute Atlas · Bhopal Claude Code Build Day · 20 September 2026
12 / 19
One 20 MW AI campus, in numbers a utility will ask about.
GRID CONNECTION AT FULL LOAD
26.0 MW
IT MW × PUE. Utilisation excluded on purpose.
ANNUAL ENERGY
1,82,208 MWh
20 × 0.8 × 1.3 × 8,760 hours.
ENERGY BILL PER YEAR
₹127.5 crore
At an assumed ₹7 per kWh.
WATER WITHDRAWAL
1,92,000 L/day
At WUE 0.5 litres per IT-kWh.
Every one of these is a claim on someone else. The DISCOM must connect 26 MW by a date. A municipality or aquifer must give up 1.9 lakh litres a day. The land must be net buildable after setbacks. A carrier must run fibre.
MW is power; MWh is energy. A 20 MW load running 24 hours uses 480 MWh. Mixing them up is the most common error in siting conversations.
Notes: Illustrative 20 MW IT campus: PUE 1.3, utilisation 0.8, WUE 0.5 L per IT-kWh, tariff INR 7/kWh. Full-load connection = IT MW x PUE = 26 MW; utilisation is excluded because the connection must carry peak. Average facility = 20.8 MW; annual = 182,208 MWh; cost = INR 127.5456 crore; water = 192,000 L/day. Assumptions, not quotations.

## Slide 13
WHERE SITING DECISIONS GO WRONG
Compute Atlas · Bhopal Claude Code Build Day · 20 September 2026
13 / 19
Context gets mistaken for commitment.
What the map or the brochure says | What it actually establishes
A high-voltage line runs past the parcel | Route context only. Not available MW, not a connection date, not redundancy.
There is a lake or river nearby | Nothing about water rights, treatment, seasonality or cooling design.
Monthly mean temperature is 35 °C | Seasonal context. Not a design-day wet-bulb; cannot size a cooling plant.
A suitability score of 84/100 | A number that hides which requirement failed and which was never checked.
The newer document says 30 MW | Newer is not authoritative. Issuer, scope, conditions and wording decide.
A broker brief promises capacity | Indicative. Not a utility feasibility letter, and that is not a connection agreement.
Notes: From the claim-check register. Each row is a real pattern in site marketing and early diligence.

## Slide 14
THE EVIDENCE PROBLEM IN INDIA
Compute Atlas · Bhopal Claude Code Build Day · 20 September 2026
14 / 19
The facts that decide a site are fragmented, and the decisive ones are private.
PUBLIC AND RETRIEVABLE
Climate climatology (NASA POWER), carrier facility inventory (PeeringDB), state boundaries (geoBoundaries).
PUBLIC BUT NOT USABLE YET
CEA power maps (access failed), NRSC Bhuvan flood hazard (no parcel extract), WRI Aqueduct water risk (basin scale).
PRIVATE, AND DECISIVE
Utility feasibility letters, sanctioned-load letters, connection agreements, land title, zoning, water allocations, broker briefs.
And the private documents disagree with each other. A broker's 30 MW and a utility's conditional 12 MW can describe the same parcel in the same month. Today that contradiction is resolved in someone's head, or not at all.
Notes: From the data plan: NASA POWER and PeeringDB were retrieved; CEA power maps failed web access; Bhuvan flood portal reachable but no parcel extract; Aqueduct documented but basin-scale. Utility letters, land title and supply agreements exist only as private documents.

## Slide 15
WHOSE DECISION THIS IS
Compute Atlas · Bhopal Claude Code Build Day · 20 September 2026
15 / 19
"Which of these sites deserves the next round of diligence, and what could invalidate it?"
FIRST CUSTOMER HYPOTHESIS
Boutique data-centre engineering and site-selection advisory firms.
An analyst uses the workspace on every shortlist; a practice head buys it. Their project documents are the private evidence public maps cannot supply.
Entry point: a paid pilot on a real three-to-six-site shortlist. A hypothesis, not a validated sale.
SECONDARY USERS AND WHAT THEY LOOK AT
Data-centre expansion teams: repeatable screening.
Investor technical-diligence teams: unresolved risks.
Industrial-park developers: what a parcel can host.
State investment-promotion teams: which infrastructure gaps recur.
Not the direct buyer: individual AI developers. They feel the constraint but do not acquire land or utility connections.
Notes: First customer hypothesis: boutique data-centre engineering and site-selection advisory firms. The analyst uses it repeatedly; the practice head buys. Secondary users listed. Avoid pitching every AI developer as the buyer: they feel the constraint but rarely acquire land or utility connections. No confirmed customers or revenue.

## Slide 16
JOBS TO BE DONE
Compute Atlas · Bhopal Claude Code Build Day · 20 September 2026
16 / 19
Five moments where the analyst needs a better instrument.
01
Several sites look attractive
Separate what is supported by evidence from what is only claimed.
02
Requirements change
Find which sites just became infeasible, and why.
03
A new document contradicts the brief
Locate the affected assumptions and recompute.
04
Diligence budget is limited
Prioritise the questions that can change the decision.
05
Time to recommend
Export a concise, traceable evidence pack.
Notes: Measure: analyst time to a sourced shortlist; hard constraints surfaced before detailed design; share of findings with valid citations; correction rate after expert review; return for a second project. Do not promise a percentage time saving before a pilot measures it.

## Slide 17
WHAT EXISTS TODAY
Source: Civarea public product page
17 / 19
Screening tools exist. None is built for this evidence problem.
Category | Examples | What we learned | The gap we see
Commercial screening | Civarea, DC Byte Site Selector | Polygon-led screening, evidence views, exports. Speed and coverage figures are vendor claims. | Not India-focused; unknowns folded into scores.
Open-source siting engines | TerraSelect (EU), CERF-DC (US), OSDCI (US), Decision Explorer | Transparent pass/fail and cost structures; EU and US data and weights. | No unknown or conflict state; no private-document reconciliation.
Advisory practice | Data-centre advisory teams at large brokerages | The workflow is real and repeated; evidence lives in documents and heads. | Manual reconciliation; nothing versioned or exportable.
India alone is not a moat. A durable advantage would need local evidence integrations, expert-reviewed workflows and measured reliability. For now these are product hypotheses, not proven unique capabilities.
Notes: Civarea: public marketing page inspected only; private product, model quality, adoption and coverage not established; its speed and coverage figures are vendor claims that do not transfer to us. Open-source engines: TerraSelect (EU, Apache-2.0), CERF-DC (US, BSD-3), Decision Explorer (MIT), OSDCI (US). None installed or executed; licenses checked from documentation. Advisory firms such as Colliers show the workflow exists. India alone is not a moat. Source: https://www.civarea.com/

## Slide 18
THREE DESIGN QUESTIONS THE PROBLEM FORCES
Compute Atlas · Bhopal Claude Code Build Day · 20 September 2026
18 / 19
Why a map, why an agent, why now.
WHY A MAP
Sites have neighbours: substations, carrier facilities, rivers, other candidates. Geography makes those relationships inspectable. It is not proof of feasibility by itself.
WHY AN AGENT
Every project brings different documents, requirements and gaps. Something has to read them, notice contradictions and decide which check comes next. The arithmetic must never be that something.
WHY NOW
Demand is projected to nearly double by 2030. India is empaneling tens of thousands of GPUs. Modular facilities widen the set of places worth investigating. More sites, same fragmented evidence.
Notes: Answers prepared for judges. Why a map: sites have geography. Why AI: documents and requirements differ per project; the model interprets and chooses investigations while numbers stay deterministic. Why now: demand growth, Indian compute access and modular options widen the set of places worth investigating.

## Slide 19
THE PROBLEM STATEMENT
Compute Atlas · Bhopal Claude Code Build Day · 20 September 2026
19 / 19
An agent that investigates whether a proposed Indian data-centre site can meet a project's requirements — and shows exactly what remains unproven.
REMEMBER 1
AI has physical requirements.
Power, cooling, water, land, fibre, time.
REMEMBER 2
Location choices combine interacting constraints.
One requirement change can flip a site.
REMEMBER 3
A good system says what it knows and what still needs proof.
Unknown is an answer. So is conflict.
Deck 2 shows how Compute Atlas does this, what we chose not to do, and what we measured.
Notes: Final problem statement from the bundle. Three things the room should remember: AI has physical requirements; location choices combine interacting constraints; an intelligent system can tell us what it knows and what still needs checking.